## B1
Construction of Office Block 1
30 Office containers +2 Ablution Units
| Works Description | Unit | Quantity | Unit price | Total price
1 | Construction / Installation works - Block 1
1.1 | Dismantling/demolition works in the shower/ablution units provided by EULEX. All the sanitary equipments, installations and existing partitions are to be dismantled/demolished. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. | EA | 2 |  | 0
1.2 | Demolition of the existing floor layers from all the office containers and ablution units (linoleum +plywood+steam blockade + insulation). Price should include transportation of debris to the city dump site. | m2 | 414.4 |  | 0
1.3 | Provide material and construct ground and first floor corridor structures consisting of iron rectangular profiles 60x40x3mm each 60cm (center to center) crosswise, and 40x2.6mm lengthwise, including L profiles 50x4mm lengthwise on both sides of the corridor, as per designs provided (pos1, pos2,pos3, pos4 dwg A-10) The whole structure elements/profiles are to be made rust free, painted with antirust paint 2x. | m2 | 112 |  | 0
1.4 | Provide material and install galvanised corrugated metal sheet 0.55mm, under the corridor structure of the ground floor, as per the designs provided (section dwg A-05). | m2 | 60 |  | 0
1.5 | Provide material and construct complete interior staircase as per design provided. Price is to include treatment with antirust paint 2x and oil pain white 2x. (dwg A-08) | LS | 1 |  | 0
1.6 | Provide material and place 100mm mineral wool insulation throughout the office containers floors /ablution unit floors/ and ground floor corridor. | m2 | 474.4 |  | 0
1.7 | Provide material and install plastic sheet 0.2mm all over the office flooring and ablution unit flooring | m2 | 414.4 |  | 0
1.8 | Provide material and install 20mm thick plywood flooring throughout the office containers and corridors - ground and first floor | m2 | 500.5 |  | 0
1.9 | Provide and install 20mm thick waterproof plywood flooring for the ablution units | m2 | 26 |  | 0
1.1 | Provide material and close up the floor strip between container joint profiles with mineral wool for double and triple rooms. | m' | 81.62 |  | 0
1.11 | Provide and install galvanised metal sheet stips 41cm wide t=2mm for covering the floor joints of double/triple office containers. | m' | 81.62 |  | 0
1.12 | Provide material and install final coat flexible vinyl/linoleum,through the floor of the office containers t=2mm, including flooring of the refurbished ablution units where the linoleum is to be 15 cm height up to the wall. Linoleum is to be welded & glued with proper adhesive. Skirtings all around the perimeter of the surface is to be included in the price. Color to be chosen by EULEX Representative. Linoleum 2.0mm thick, commercial use, EN 649, classification as per EN 685 Class 33, areas with heavy traffic. | m2 | 420 |  | 0
1.13 | Provide material and install laminate flooring for the corridors surface, suitable for commercial use, resistant to scratches and water, with 5mm sponge underlayer , th =10mm. Price to include appropriate skirting profiles throught the building and also aluminium skirting at offices entrance/building entrance. Sample to be provided for approval prior to installation. | m2 | 112 |  | 0
1.14 | Provide material and construct corridor facade walls/staircase facade walls with the following materials: interior with plasterboards 2x12.5mm over metal studs, thermal insulation 100mm, metal structure 40mmx60mm as supporting structure, OSB plate 15mm, membrame foil 0.2mm, covered with metal sheet prepainted thickness 0.55mm as a facade from outside. Price shall include treatment of plaster boards and preparation of the surface for painting. Openings for foreseen doors and windows is to be prepared as per designs provided (dwg A-10, detail) | m2 | 14.4 |  | 0
1.15 | Provide material and construct first class quality wood roof structure as per designs provided (dwg A-06) Slope 21% on both sides. All joint metal elements shall be galvanized. Nails, screws, bolts and nuts shall be of stainless steel. | m2 | 334.25 |  | 0
1.16 | Provide and install pre-painted corrugated metal sheet of t=0.55mm as roof cover, Price to include snow guards. Color RAL 9002. Slope surface calculated. | m2 | 344.6 |  | 0
1.17 | Provide and install pre-painted flat metal sheet roof eaves 50 cm overhang, of 0.50mm thickness. Color RAL 9002 (fascia and soffit all sides). | m2 | 56.6 |  | 0
1.18 | Provide and install half round horizontal rain gutters 120mm, from pre-painted metal sheet 0.6mm thickness. Color RAL9002. Price shall include as well provision and installation of hangers and all the required accessories. | m' | 50.12 |  | 0
1.19 | Provide and install vertical gutters ( Rainwater down pipes), of pre-painted metal sheet 0.6mm thicknes. Color RAL 9002. | m' | 44.8 |  | 0
1.2 | Provide and install pre-painted metal sheet roof edges/A sides 0.50mm thickness (piano). Color RAL 9002. Price shall include the required flushings where the two different height roofs meet and the roof ventilation grill. | m2 | 24 |  | 0
1.21 | Provide material and seal the joints between containers for the double and triple container rooms (walls/ceiling). Sealing is to be done with pre-painted flat metal sheet thickness 0.60mm. Prior to installation the gaps between two containers are to be filled with foam/mineral wool as required. Color similiar to interior paint. | m' | 147.5 |  | 0
1.22 | Provide and install 10cm mineral wool throughout the ceiling of the corridor- first floor, including supporting timber structure (80x100mm) as per dwg provided (A-05) | m2 | 60 |  | 0
1.23 | Provide and install plastic sheet 0.2mm throught the ceiling of the corridor of the first floor. | m2 | 60 |  | 0
1.24 | Provide and install mineral fiber suspended ceiling panels dim 60x60 cm, first class quality, complete with all the necessary fixtures/supporters for the ground and first floor corridor. Sample to be provided for approval prior to installation. | m2 | 112 |  | 0
1.25 | Provide material and paint interior of all office/ablution units, including corridors with acrylic enamel paint 2x. Paint charcteristics: semi-gloss coating, eco-friendly, without unpleasent odor, thinning with water. Paint is to be applied by spraying. Previosly the surface is to be cleaned of dust and any debris. | m2 | 1557.78 |  | 0
1.26 | Provide material and paint exterior of the building/containers with oil paint 2x, (spraying) color white, previosly cleaning the surface of dust and any debris. Any corroded area is to be treated initially with anti rust paint. | m2 | 340.8 |  | 0
1.27 | Provide and install external PVC double wing door.The main entrance door should be of PVC profiles door as per design provided (dwg. A-11) DIM 180/240cm Glass: double, fully insulated, with noise reduction and thermal protection, 6+16+6mm. Door is to be equipped with door lock complete, minimum three keys. | EA | 2 |  | 0
1.28 | Provide and install metal solid door as emergency exit door, equipped with anit panic push bar, with handle and possibility to close with a key from outside, dim 90x205cm (dwg A-11) | EA | 2 |  | 0
1.29 | Provide and install corridor PVC Windows DIM 90x110cm. Glass: double, fully insulated, with noise reduction and thermal protection 6+16+6mm. (dwg A-11) | EA | 3 |  | 0
1.3 | Provide and install staircase PVC Window dim 120x270cm, as per design provided. Glass: double, fully insulated, with noise reduction and thermal protection, 6+16+6mm (dwg A-11) | EA | 1 |  | 0
1.31 | Install window type AC Units of 12000BTU in each office containers. AC window type units will be provided by EULEX. Contractor is to provide all the other required materials for connection. | EA | 30 |  | 0
1.32 | Provide material and close the gaps around the new installed AC Units (30). Due to difference on the size of the existing AC window and the provided AC Units the gaps remained are to be closed. Gaps should be closed with pre-painted flat sheet 0.6mm from both sides, white color/similar to containers color, and filled with extruded rigid polystyrene foam in-between. | LS | 1 |  | 0
1.33 | Provide and replace all door cyilinders (offices and ablution units). New cyilinders should have minimum three keys, adjucting also the existing door lock. | EA | 20 |  | 0
1.34 | Provide and install internal aluminium venetian blinds - of 16mm wide strips, with single wand mechanism for blind lift and tilt, for all the windows in the building. Color to be chosen by EULEX Representative. | m2 | 75.6 |  | 0
1.35 | Provide and install toilet partition walls made of PVC, full panels , in which PVC doors in width of 70cm /195cm door are built-in , furnished with a toilet lock (free/occupied), toilet walls are lifted from the floor by 150 mm, fixed on galvanised or painted bearers, except the middle wall dividing male female toilet which should be from floor to ceiling. Colour of the walls and doors white Remark : Number and arrangement according to the enclosed drawing . | m2 | 20.77 |  | 0
1.36 | Provide and install extractor fan 100mm diameter for ablution units | EA | 2 |  | 0
1.37 | Provision and installation of room numbers (01 to 16) | EA | 16 |  | 0
1.38 | Provide material, manufacturing and installation of the main entrance stairs and shed as per the provided design (dwg A-07). All metal profiles have to be treated with anti rust paint 2x and the final paint coat 2x. Prior to manufacturing all measurements must be taken on spot. The shed shall be covered with prepainted corrugated sheet including horizontal and vertical gutters. | LS | 1 |  | 0
1.39 | Provision of materials, manufacturing and installation of Emergency exit staircase from the first floor, as per designs/details provided (dwg A-09). All metal profiles have to be treated with anti rust paint 2x and the final oil paint coat 2x. Prior to manufacturing all measurements must be taken on spot. | LS | 1 |  | 0
1.4 | Provision of materials, manufacturing and installation of Emergency Exit stair of the ground floor. All metal profiles have to be treated with anti rust paint 2x and the final paint coat 2x. | LS | 1 |  | 0
|  |  |  | Total 1 | 0
2 | Electrical Works | Unit | Quantity
2.1 | Dismantling of the existing electrical/IT installations within the provided EULEX office containers. All the materials dismantled ( switches, lights, plugs) are to be handed over to EULEX Representative. Individual containers electrical panels are to not be dismantled, but to remain and be reused. Clearance for any removal of debris from the site is to be taken from the Project Manager of EULEX. | EA | 32 |  | 0
2.2 | Install main electrical panel for the building, complete. Electrical panel will be provided by EULEX .Price to include grounding of the panel and the required materials. | EA | 1 |  | 0
2.3 | Provide material and install containers electrical connections (maximum 4 containers on a line), for the whole containerised building. Connections are to be done with cabling flexible 5x6mm2, including industrial plugs and sockets of 32A, 5 pin, for each container as required, to the main electrical panel. | EA | 32 |  | 0
2.4 | Provide material and install earthing of containerised building in all four angles. ( 2m' copper rods with connection of containers in between with cable 1x35mm2) | LS | 1 |  | 0
2.5 | Provide and install single phase double socket outlets, wall/panel mounted, 16A, 220V. Price shall include the - Cable type PPY 3x2,5mm² and all the required fittings for functional sockets. Cables are to be covered with proper PVC trunkings. | EA | 95 |  | 0
2.6 | Provide and install single phase single sockets, complete with required fittings 16A, 220V. Price shall include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC trunking. | EA | 38 |  | 0
2.7 | Provide and install fluorescent light fittings designed for suspended ceiling: - 4x18W / dim (60x60)cm, throught the corridor of the building. Price shall including provision and installation of required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be placed over the suspended ceiling. | EA | 23 |  | 0
2.8 | Provide and install ceiling mounted fluorescent lights 2x36W. Price shall include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking. | EA | 60 |  | 0
2.9 | Provide and install ceiling mounted fluorescent lights 1x36W. Price shall include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking. | EA | 4 |  | 0
2.1 | Provide and install ceiling mounted fluorescent lights 2X36W, water resistant, for the entrance shed. | EA | 1 |  | 0
2.11 | Provide and install ceiling mounted fluorescent lights 1x18W. Price shall include also provision and installation of the required cabling for functional lights - cable type PPY3x1.5mm2. Cabling is to be covered with proper PVC trunking. | EA | 8 |  | 0
2.12 | Provide and install cabling for the Emergency EXIT lights as per dwg provided, 8W. Price shall include all the required trunking, and any other required fittings for the installation. Emergency Exit lights will be provided by EULEX. | EA | 3 |  | 0
2.13 | Provide and install cabling for the emergency lights 2 x8W as per dwg provided, including all the trunking required and protection. Emergency lights will be provided by EULEX. | EA | 6 |  | 0
2.14 | Supply and install light switches 6A (single/double pole, and alternative ) mounted on wall panels . | EA | 22 |  | 0
2.15 | Provide and install PVC container distribution box, mounted indoors on ceiling near the window with space for 12 fuses fitted with: 5 EA -16A fuses, 1EA - 20A Fuse, protection fid 3P/40A 300mA. Note: As container provided by EULEX will be used/old office containers this position is as optional for installation of panels if missing) | EA | 10 |  | 0
2.16 | Provide and install electrical panel with 3 poles circuit breaker 32A, with supply cable 5x6mm2 from the main electrical panel. Positioning of the panel as per layout provided, required for the IT Rack Cabinet. | EA | 1 |  | 0
2.17 | Provide material and install external street lights 125W in corners of the building, as indicated in the provided layouts. Lights are to be installed in galvanised metal poles fixed on the structure of the containers. Price to include circuit breakers, dark sensor, and other fittings as required. | EA | 4 |  | 0
|  |  |  | Total 2 | 0
TOTAL BLOCK 1
1 | Construction/Installation Works Total | 0
2 | Electrical Works Total | 0
| Total all | 0

## B2
Construction of Office Block 2
30 Office containers +2 Ablution Units
| Works Description | Unit | Quantity | Unit price | Total price
1 | Construction / Installation works - Block 1
1.1 | Demolition of the existing floor layers from all the office containers (linoleum +plywood+steam blockade+insulation). Price should include transportation of debris to the city dump site. | m2 | 388.5 |  | 0
1.2 | Provide material and construct ground floor and first floor corridor structures consisting of metal profiles 60x40x3mm each 60cm crosswise, and 40x2.6mm lengthwise, including L profiles 50x4mm lengthwise on both sides of the corridor, as per designs provided (dwg A-10). All metal profiles are to be made rust free, painted with antirust paint 2x | m2 | 112 |  | 0
1.3 | Provide material and install galvanised corrugated sheet 0.55mm, under the corridor structure of the ground floor, as per the designs provided (section dwg A-05). | m2 | 60 |  | 0
1.4 | Provide material and construct complete interior staircase as per design provided. Price to include treatment with antirust paint 2x and oil paint white 2x (dwg A-08) | LS | 1 |  | 0
1.5 | Provide material and place 100mm mineral wool insulation throughout the office containers floors / and ground floor corridor. | m2 | 448.5 |  | 0
1.6 | Provide material and install plastic sheet 0.2mm all over the office flooring | m2 | 388.5 |  | 0
1.7 | Provide material and install 20mm thick plywood flooring throughout the office containers and corridors - ground and first floor | m2 | 500.5 |  | 0
1.8 | Provide material and close up the floor strip between container joint profiles with mineral wool for double and triple rooms. | m' | 81.62 |  | 0
1.9 | Provide and install galvanised metal sheet stips 41cm wide t=2mm for covering the floor joints of double/triple office containers. | m' | 81.62 |  | 0
1.1 | Provide material and install final coat flexible vinyl/linoleum,throught the floor of the office containers t=2mm. Linoleum is to be welded & glued with proper adhesive. Skirtings all around the perimeter of the surface is to be included in the price. Color to be chosen by EULEX Representative. Linoleum 2.0mm thick, commercial use, EN 649, classification as per EN 685 Class 33, areas with heavy traffic. | m2 | 388.5 |  | 0
1.11 | Provide material and install laminate flooring for the corridors surface, suitable for commercial use, resistant to scratches and water, with 5mm sponge underlayer , th =10mm. Price to include appropriate skirting profiles throught the building and also aluminium skirting at offices entrance/building entrance. Sample to be provided for approval prior to installation. | m2 | 112 |  | 0
1.12 | Provide material and construct corridor walls/staircase facade walls with the following materials: interior with plasterboards 2x12.5mm over metal studs, thermal insulation 100mm, metal structure 40mmx60mm as supporting structure, OSB plate 15mm, membrame foil, covered with metal sheet prepainted thickness 50mm (piano) as a facade from outside. Price shall include treatment of plaster boards and preparation of the surface for painting. Openings for foreseen doors and windows is to be prepared as per designs provided. | m2 | 14.4 |  | 0
1.13 | Provide material and construct first class quality wood roof structure as per designs provided (dwg A-06) Slope 21% on both sides. All joint metal elements shall be galvanized. Nails, screws, bolts and nuts shall be of stainless steel. | m2 | 334.25 |  | 0
1.14 | Provide and install pre-painted corrugated metal sheet of t=0.55mm as roof cover, Price to include snow guards and . Color RAL 9002. Slope surface calculated. | m2 | 344.6 |  | 0
1.15 | Provide and install pre-painted flat metal sheet roof eaves 50 cm overhang, of 0.50mm thickness. Color RAL 9002 (fascia and soffit all sides). | m2 | 56.6 |  | 0
1.16 | Provide and install half round horizontal rain gutters 120mm, from pre-painted metal sheet 0.6mm thickness. Color RAL9002. Price shall include as well provision and installation of hangers and all the required accessories. | m' | 50.12 |  | 0
1.17 | Provide and install vertical gutters ( Rainwater down pipes), of pre-painted metal sheet 0.6mm thicknes. Color RAL 9002. | m' | 44.8 |  | 0
1.18 | Provide and install pre-painted metal sheet roof edges/A sides 0.50mm thickness (piano). Color RAL 9002. Price shall include the required flushings where the two different height roofs meet and the roof ventilation grill. | m2 | 24 |  | 0
1.19 | Provide material and seal the joints between containers for the double and triple container rooms (walls/ceiling). Sealing is to be done with pre-painted flat metal sheet thickness 0.60mm. Prior to installation the gaps between two containers are to be filled with foam/mineral wool as required. Color similiar to interior paint. | m' | 147.5 |  | 0
1.2 | Provide and install 10cm mineral wool throughout the ceiling of the corridor- first floor, including supporting timber structure (80x100mm) as per dwg provided (A-05). | m2 | 60 |  | 0
1.21 | Provide and install plastic sheet 0.2mm throught the ceiling of the corridor of the first floor. | m2 | 60 |  | 0
1.22 | Provide and install mineral fiber suspended ceiling panels dim 60x60 cm , first class quality, complete with all the necessary fixtures/supporters for the ground and first floor corridor. Sample to be provided for approval prior to installation. | m2 | 112 |  | 0
1.23 | Provide material and paint interior of all office/ablution units, including corridors with acrylic enamel paint 2x. Paint charcteristics: semi-gloss coating, eco-friendly, without unpleasent odor, thinning with water. Paint is to be applied by spraying. Previosly the surface is to be cleaned of dust and any debris. | m2 | 1557.78 |  | 0
1.24 | Provide material and paint exterior of the building/containers with oil paint 2x, (spraying) color white, previosly cleaning the surface of dust and any debris. Any corroded area is to be treated initially with anti rust paint. | m2 | 340.8 |  | 0
1.25 | Provide and install external PVC double wing door.The main entrance door should be of PVC profiles door as per design provided (dwg A-11). DIM 180/240cm Glass: double, fully insulated, with noise reduction and thermal protection, 6+16+6mm. Door is to be equipped with door lock complete, minimum three keys. | EA | 2 |  | 0
1.26 | Provide and install metal solid door as emergency exit door, equipped with anti panic push bar, with handle and possibility to close with a key from outside, dim 90x205cm (dwg A-11) | EA | 2 |  | 0
1.27 | Provide and install corridor PVC Windows DIM 90x110cm. Glass: double, fully insulated, with noise reduction and thermal protection 6+16+6mm. (dwg A-11) | EA | 3 |  | 0
1.28 | Provide and install staircase PVC Window dim 120x270cm, as per design provided (dwg A-11). Glass: double, fully insulated, with noise reduction and thermal protection, 6+16+6mm | EA | 1 |  | 0
1.29 | Install window type AC Units of 12000BTU in each office containers. AC window type units will be provided by EULEX. Contractor is to provide all the other required materials for connection. | EA | 30 |  | 0
1.3 | Provide material and close the gaps around the new installed AC Units (30). Due to difference on the size of the existing AC window and the provided AC Units the gaps remained are to be closed. Gaps should be closed with pre-painted flat sheet 0.6mm from both sides, white color/similar to containers color, and filled with extruded rigid polystyrene foam in-between. | LS | 1 |  | 0
1.31 | Provide and replace all door cyilinders (offices and ablution units). New cyilinders should have minimum three keys, adjucting also the existing door lock. | EA | 20 |  | 0
1.32 | Provide and install internal aluminium venetian blinds - of 16mm wide strips, with single wand mechanism for blind lift and tilt, for all the windows in the building. Color to be chosen by EULEX Representative. | m2 | 75.6 |  | 0
1.33 | Relocate extractor fans of the ablution units from the interior to the outside perimeter wall, including closure of the previous position hole on the interior wall witrh prepainted metal sheet on both sides filled with insulation. | EA | 2 |  | 0
1.34 | Provision and installation of room numbers (01 to 16) | EA | 16 |  | 0
1.35 | Provide material, manufacturing and installation of the main entrance stairs and shed as per the provided design (dwg A-07). All metal profiles have to be treated with anti rust paint 2x and the final paint coat 2x. Prior to manufacturing all measurements must be taken on spot. The shed shall be covered with prepainted corrugated sheet including horizontal and vertical gutters. | LS | 1 |  | 0
1.36 | Provision of materials, manufacturing and installation of emergency exit staircase from the first floor, as per designs/details provided (A-09). All metal profiles have to be treated with anti rust paint 2x and the final paint coat 2x. Prior to manufacturing all measurements must be taken on spot. | LS | 1 |  | 0
1.37 | Provision of materials, manufacturing and installation of Emergency Exit stair of the ground floor as per dwg provided. All metal profiles have to be treated with anti rust paint 2x and the final paint coat 2x. | LS | 1 |  | 0
|  |  |  | Total 1 | 0
2 | Electrical Works | Unit | Quantity
2.1 | Dismantling of the existing electrical/IT installations within the provided EULEX office containers. All the materials dismantled ( switches, lights, plugs) are to be handed over to EULEX Representative. Individual containers electrical panels are to not be dismantled, but to remain and be reused. Clearance for any removal of debris from the site is to be taken from the Project Manager of EULEX. | EA | 30 |  | 0
2.2 | Install main electrical panel for the building, complete. Electrical panel will be provided by EULEX. Price to include grounding of the panel and the required materials. | EA | 1 |  | 0
2.3 | Provide material and install containers electrical connections (maximum 4 containers on a line), for the whole containerised building. Connections are to be done with cabling 5x6mm2, including industrial plugs and sockets of 32A, 5 pin, for each container as required, to the main electrical panel. | EA | 32 |  | 0
2.4 | Provide material and install earthing of containerised building in all four angles. ( 2m' copper rods with connection of containers in between with cable 1x35mm2) | LS | 1 |  | 0
2.5 | Provide and install single phase double socket outlets, wall/panel mounted, 16A, 220V. Price shall include the - Cable type PPY 3x2,5mm² and all the required fittings for functional sockets. Cables are to be covered with proper PVC trunkings. | EA | 95 |  | 0
2.6 | Provide and install single phase single sockets, complete with required fittings 16A, 220V. Price shall include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC trunking. | EA | 30 |  | 0
2.7 | Provide and install fluorescent light fittings designed for suspended ceiling: - 4x18W / dim (60x60)cm, throught the corridor of the building. Price shall including provision and installation of required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be placed over the suspended ceiling. | EA | 23 |  | 0
2.8 | Provide and install ceiling mounted fluorescent lights 2x36W. Price shall include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking. | EA | 60 |  | 0
2.9 | Provide and install ceiling mounted fluorescent lights 2X36W, water resistant, for the entrance shed. | EA | 1 |  | 0
2.1 | Provide and install cabling for the Emergency EXIT lights as per dwg provided, 8W. Price shall include all the required trunking, and any other required fittings for the installation. Emergency Exit lights will be provided by EULEX. | EA | 2 |  | 0
2.11 | Provide and install cabling for the emergency lights 2 x8W as per dwg provided, including all the trunking required and protection. Emergency lights will be provided by EULEX. | EA | 6 |  | 0
2.12 | Supply and install light switches 6A (single/double pole, and alternative ) mounted on wall panels . | EA | 18 |  | 0
2.13 | Provide and install PVC container distribution box, mounted indoors on ceiling near the window with space for 12 fuses fitted with: 5 EA -16A fuses, 1EA - 20A Fuse, protection fid 3P/40A 300mA. Note: As container provided by EULEX will be used/old office containers this position is as optional for installation of panels if missing) | EA | 10 |  | 0
2.14 | Provide and install electrical panel with 3 poles circuit breaker 32A, with supply cable 5x6mm2 from the main electrical panel. Positioning of the panel as per layout provided, required for the IT Rack Cabinet. | EA | 1 |  | 0
2.15 | Provide material and install external street lights 125W in corners of the building, as indicated in the provided layouts. Lights are to be installed in galvanised metal poles fixed on the structure of the containers.Price to include circuit breakers, dark sensor, and other fittings as required. | EA | 2 |  | 0
|  |  |  | Total 2 | 0
TOTAL BLOCK 1
1 | Construction/Installation Works Total | 0
2 | Electrical Works Total | 0
| Total all | 0

## Infrastructure and other
Infrastructure and other outside works
1 | Roads and parking | Unit | Quantity | Unit Price | Total Price
1.1 | Conduct site survey | LS | 1 |  | 0
1.2 | Machine excavation of top layer of soil in thickness average ~50cm, including leveling the surface, spraying the subgrade with water spraying and compacting the same with power roller maintaining the slope. Price shall include removal of soil from site and transportation of the same outside the Compound to a designated city dump site. | m3 | 3780.5 |  | 0
1.3 | Providing and laying of geotextile(300g/m²) on the compacted soil surface as described above with an overlap of 50mm at junction and between sheets, foreseen for the surface to be asphalted. | m2 | 2847 |  | 0
1.4 | Providing and spreading gravel 0-60mm to form the 30cm thick sub-base course. Spread and compact the gravel in 100mm thick layers to a finished requested thickness. | m3 | 2268.3 |  | 0
1.5 | Providing and spreading gravel 0-30 mm on previously compacted gravel sub-base as described under item No.1.4 above and compacting to form a final base course of 20cm thickness. Compacting to be done with power roller. | m3 | 1512.2 |  | 0
1.6 | Provide and spread layer of bitumen emulsion (hot coat) above base course, average 0,8kg/m2 for better connection between road base course and layer of asphalt. | m2 | 2847 |  | 0
1.7 | Provide material and laying of asphalt layer thickness 80mm, mixture 0-16mm including compaction. | m2 | 2847 |  | 0
1.8 | Provision and installation of concrete curb stones dim 30x15cm, along the roads and parking areas as specified in the drawings. | m' | 374.5 |  | 0
1.9 | Provision and installation of the curb stones dim 100x30x8 cm around the office buildings. | m' | 174.9 |  | 0
1.1 | Provide material, laying and machine compaction of sand in thickness d= 5cm for the pathways and parking areas, over the compacted gravel indicated under item no.1.5 | m2 | 2344 |  | 0
1.11 | Provide material and laying of pavement blocks 20x10x8cm over the sand layer, filling also the joints with sand. | m2 | 2344 |  | 0
1.12 | Provide material and marking/painting of all the signs/lines/pedestrian crossings on the newly laid pavements,as shown in the drawing, by using thermoplastic paint that contains sufficient pellicle-spraying high- quality glass micro beads with stable reflection. | LS | 1 |  | 0
1.13 | Provide and spread river washed stones around the two office blocks strip sorrounding area as per dwg provided th=20cm | m3 | 21.8 |  | 0
1.14 | Provide and lay soil for the foreseen green areas, price is to include seeding of grass and plants as forseen in the provided design/layout. | m2 | 46.8 |  | 0
|  |  |  | Total | 0
2 | Electrical | Unit | Quantity | Unit Price | Total Price
2.1 | Provide material and construct transformer reinforced concrete base, dim 230x390,th=20cm including grounding, with the required manhole deep 120cm as per designs provided (dwg A-22). Note: Transformer of 400KVA will be provided and installed on site by EULEX. | LS | 1 |  | 0
2.2 | Install main electrical panel (#1 indicated in the dwg E-01), close to the transformer. The electrical panel complete will be provided by EULEX. Price to include grounding of the panel and the required materials. | EA | 1 |  | 0
2.3 | Install main electrical panel (#2 indicated in dwg E-01), close to the transformer. The electrical panel complete will be provided by EULEX. Price to include grounding of the panel and the required materials. | EA | 1 |  | 0
2.4 | Excavation of trenches up to depth of 100cm for the underground cabling, as per designs provided. (60x100cm), including backfilling/compaction and removal of surplus from the site. | m3 | 173.2 |  | 0
2.5 | Excavation of trenches up to depth of 60cm for the street lights underground cabling, as per designs provided. (50x60cm), including backfilling/compaction and removal of surplus from the site. | m3 | 42.6 |  | 0
2.6 | Provide material and laying of sand base (under, around and over the ducting pipes) throughout the all trenches. | m3 | 66.3 |  | 0
2.7 | Laying of ducting pipes Ø100mm, (4 pipes per trench) from transformer/panels through manhole #1 up to #11. Note: Ducting pipes for this trench/route will be provided by EULEX. | m' | 223 |  | 0
2.8 | Supply and laying of the underground warning tape throughout the all trenches. | m' | 430.5 |  | 0
2.9 | Provide and install precast concrete manholes complete 1000 depth dim1000x1000m , including heavy duty metal covers 600x600mm (25T) and other required works to make the manholes functional | EA | 11 |  | 0
2.1 | Provide material and install underground cable 4x240mm2 (Al) from electrical panel #1 through manhole#1 up to Block #2 panel.Price to include connection of the cables in both ends and all the needed fittings | m' | 76.65 |  | 0
2.11 | Provide material and install underground cable 4x185mm2 (Al) from electrical panel of block #2 through manhole 6 up to block #1 main electrical panel. Price to include connection of the cables in both ends and all the needed fittings | m' | 32 |  | 0
2.12 | Provide material and install underground cable 4x25mm2 (Al) from main electrical panel of Block #1 to electrical panel of Rub Hall 3. Price to include connection of the cables in both ends and all the needed fittings. | m' | 31.45 |  | 0
2.13 | Provide material and install undergroung cable 4x125 (Al)mm2 from Main Electrical Panel #2 to the Hardwall Structures through the trenches. Price to include connection of the cables in both ends and all the needed fittings | m' | 67.4 |  | 0
2.14 | Provide material and install underground cabling 4x35mm2 (Al)from Harwalls electrical panel to Rub Hall 2&3 electrical panel. Price to include connection of the cables in both ends and all the needed fittings | m' | 26.5 |  | 0
2.15 | Provide and install underground cabling 5x6mm2 Cu from Panel #2 up to heating container electrical panel. Price to include connection of the cables in both ends and all the needed fittings | m' | 42.3 |  | 0
2.16 | Provide and install underground cable for the street lights (point 2.23 below), 5x4mm2 NYY-J, including ducting pipe Ø50 from block 2 electrical panel direction main gate. Price to include connection of the cables and all the needed fittings as required for functional lights including dark sensors. | m' | 88 |  | 0
2.17 | Provide and install underground cable for the street lights (point 2.23 below), 5x4mm2 NYY-J, including ducting pipe Ø50mm from electrical panel #1 towards manhole #10. Price to include connection of the cables and all the needed fittings as required for functional lights including dark sensors. | m' | 121.9 |  | 0
2.18 | Provide and install underground cable for the street lights (point 2.23 below), 5x4mm2 NYY-J, including ducting pipe Ø50mm from electrical panel #1 beside the main road sidewalk. Price to include connection of the cables and all the needed fittings as required for functional lights including dark sensors. | m' | 103.5 |  | 0
2.19 | Provide and Install underground cable 4x70mm2 Cu from panel #1 up to the server room container and from the server room container up to the old transformer on site. | m' | 58.2 |  | 0
2.2 | Provide material and install grounding protection for street lights. Grounding strip FeZn 25x4mm throughout the length, price to include related fittings and connectors. | m' | 247.4 |  | 0
2.21 | Provide and install decorative street lights h=320cm complete, IP44 protection, two luminairies of Ø 400mm, 2x75 energy saving bulbs. Sample to be provided for approval prior to installation on site. | EA | 22 |  | 0
2.22 | Provide and install duct pipe Ø75mm from manholes to each building/heating plant/server container ( 3 per each building). | m' | 175 |  | 0
2.23 | Cutting and removal of asphalt/pathway/curbs to create a space for cable trenches opening from server room container to the old transformer. This work include supply of material and re-asphalt/pavement works of the previously removed surfaces, after finishing the cable laying. ( ~100cm wide) | m' | 7.5 |  | 0
2.24 | Connecting manhole #1 with existing manhole on site nearby. Price to include laying of 4 Ø100mm ducting pipes, digging/backfilling works and laying of warning tape. Ducting pipes will be provided by EULEX . Distance m'~8m from manhole 1 | LS | 1 |  | 0
|  |  |  | Total | 0
3 | Desing and Build New Heating Plant/System for the office buildings,hardwalls and rubhalls | Unit | Quantity | Unit Price | Total Price
3.1 | Desing and Build New Heating System for the new Compound, in accordance with: DIN-EN 12831 and DIN-14336 and technical specifications provided. Buildings to be covered with Design and Build are : Office Block 1, Office Block 2,Rub Halls 1&2&3, Hardwalls 1&2. Note: EULEX will be providing complete containerised bolier room equipped as below: - Boiler Thermostahl type EN500 - Burner Ecoflame 415V-670 50Hz - 4 Circulation Pumps Grundfos 3 X400-415 V 50Hz (Power 1100 -1550W) - Expantion tank for pressure control volume 500ltr - Ionic water softner - Command panel Also EULEX will provide all the radiators for the office buildings ( Block 1, 2) different sizes and other circulation pumps if foreseen with the design. Any other equipment and materials required for a functional heating system installation are to be provided by the contractor including 5000ltr fuel tank which is to be installed underground. | LS | 1 |  | 0
|  |  |  | Total | 0
Infrastructure and other
1 | Roads and Parkings | 0
2 | Electrical Works | 0
3 | Heating Plant/System | 0
| Total all | 0

## Rub Halls 1,2&3
Erection of Rubb Hall Units
Rubb Hall 1,2 &3
| Works Description | Unit | Quantity | Unit price | Total price
1 | Earth Works
1.1 | Excavating of strip foundation trenches for all Rubb Hall Units (Rubb Hall 1, 2 &3) as per the designs provided (dwg A-18, A-19) | LS | 1 |  | 0
1.2 | Provision of material, filling and compaction of strip foundations trenches with gravel, thickness 10cm . Filling of the ground beneath is to be done by first compacting the existing ground. | m3 | 5.28 |  | 0
1.3 | Backfilling of soil/gravel around the foundation strip after construction of foundation, and removal of surplus material from site. | LS | 1 |  | 0
2 | Reinforcement and Concrete Works
2.1 | Provision of material and installation of formworks for the strip foundations, including all the required accessories. | m2 | 210.24 |  | 0
2.2 | Provision of materials and installation of reinforcement as per specifications/drawings provided (using bars of Ø10 mm, Ø12 mm) (dwg A-18, A19) | kg | 1326.12 |  | 0
2.3 | Provision of materials and installation of reinforcement as per specifications/drawings provided (using bars of Ø8 mm) | kg | 679.27 |  | 0
2.4 | Provision of material and concreting of the reinforced strip foundation with concrete C-30. Note: concrete quality lab tests are to be conducted for the used concrete ( cubes 150x150x150mm >28days) | m3 | 31.5 |  | 0
3 | Lightning Protection
3.1 | Provide material and install lightning protection. Grounding is to be provided in the horizontal reinforcement of the foundation with FeZn strips of size 40x4mm throughout the perimeter, with 1 meter strip extensions in all four corners, price to include crosswise elements, related fittings and connections, and earth rods 1.5m in all 4 angles the three Rubb Hall Units. ( as per designs provided dwg A-18, A-19). | LS | 1 |  | 0
4 | Rubb Halls Erection Works
4.1 | Assemble Rubb Hall Units size 10mx24m comprising of galvanised steel structures (2) and aluminium structure (1) in sections of 4m center to center, coated with PVC polyester coating tensioned over the steel structure. The Rubb Hall Units will be provided by EULEX and are to be erected over the strip foundation, as per assembly guide provided for Rubb Hall 3 and the designs provided for all the three Rubb Halls. | EA | 3 |  | 0
4.2 | Provide and install metal solid door as emergency exit door, equipped with anti panic push bar, with handle and possibility to close with a key from outside, dim 90x205cm. Price has to include metal frame construction works for the door within the RubbHall structure, with proper flushings and cover. | EA | 2 |  | 0
4.3 | Provision and laying of plastic foil 0.2mm all over the floor surface. | m2 | 692.6 |  | 0
4.4 | Provide material and construct reinforced concrete slab for all three Rubb Halls th=15cm with C-30, net Q335 Ø8mm 15x15, over the compacted graveled surface ( Note: gravel layers 0-60, 0-30 are included within the infrastructure works). | m3 | 103.89 |  | 0
4.5 | Provide and lay the finishing layer with Fer-concrete (Ferrobeton) in two stages. The processing to be done by machine trowel until the mixture is completely pushed into the fresh concrete. (finishing is performed by rotating floats "helicopters" up to complete smoothing of surface) . Edge parts are finalized manually by float. Dilatation pointing: The joints are about 0.3 cm wide.The joints depth 25% of the slab thickness, filled with polyurethane masses after complete drying of concrete. | m2 | 692.6 |  | 0
5 | Electrical Works
5.1 | Install main electrical panel for Rubb Hall 1&2, complete, including grounding of the panel. Electrical panel will be provided by EULEX . | LS | 1 |  | 0
5.2 | Install main electrical panel for Rubb Hall 3 , complete, including grounding. Electrical panel will be provided by EULEX . | LS | 1 |  | 0
5.3 | Provide and install double tube florescent light with top cover (bracket) 2x36W. Price shall include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC ducting pipes or cover. Product suitable for use in warehouses. Lights to be organized in 4 separate lines per building. | EA | 68 |  | 0
5.4 | Provide and install cabling for the Emergency EXIT lights as per dwg provided, 8W. Price shall include all the required trunking/ducting, and any other required fittings for the installation. Emergency Exit lights will be provided by EULEX. | EA | 4 |  | 0
5.5 | Provide and install cabling for the emergency lights 2 x8W as per dwg provided, including all the trunking required and protection. Emergency lights will be provided by EULEX. | EA | 18 |  | 0
5.6 | Provide material and install external street lights 125W in corners of the building, as indicated in the provided layouts. Lights are to be installed in galvanised metal poles fixed on the structure/or with galvanised metal poles fixed to the ground. | EA | 4 |  | 0
5.7 | Provide and install rotary light switches | EA | 8 |  | 0
5.8 | Provide material and install three phase socket, complete with all the required fittings. All the cabling is to be covered with proper PVC trunking/ducting. | EA | 4 |  | 0
5.9 | Provide and install single phase double socket outlets, wall/panel mounted, 16A, 220V. Price shall include the - Cable type PPY 3x2,5mm² and all the required fittings for functional sockets. Cables are to be covered with proper PVC trunkings. | EA | 4 |  | 0
|  | Total all |  |  | 0
Note: | Prior to commencing the foundation works, the contractor is to check the issued Rubb Hall Units and verify the dimensions of the structure.

## Hardwalls 1&3
Erection of Harwall Structures
Hardwalls 1&2
| Works Description | Unit | Quantity | Unit price | Total price
1 | Earth Works
1.1 | Excavating of strip foundation trenches for the Harwall Units as per the designs provided. (dwg A-21) | LS | 1 |  | 0
1.2 | Provision of material, filling and compaction of strip foundations trenches with gravel, thickness 10cm . Filling of the ground beneath is to be done by first compacting the existing ground. | m3 | 3.67 |  | 0
1.3 | Backfilling of soil/gravel around the foundation strip after construction of foundation, and removal of surplus material from site. | LS | 1 |  | 0
2 | Reinforcement and Concrete Works
2.1 | Provision of material and installation of formworks for the strip foundations, including all the required accessories. | m2 | 146.35 |  | 0
2.2 | Provision of materials and installation of reinforcement as per specifications/drawings provided ( using bars of Ø10 mm, Ø12 mm) | kg | 871.32 |  | 0
2.3 | Provision of materials and installation of reinforcement as per specifications/drawings provided ( using bars of Ø8 mm) (dwg A-21) | kg | 474.37 |  | 0
2.4 | Provision of material and concreting of the reinforced strip foundation with concrete C-30. Note: concrete quality lab tests are to be conducted for the used concrete ( cubes 150x150x150mm >28days) | m3 | 22.08 |  | 0
3 | Lightning Protection
3.1 | Provide material and install lightning protection. Grounding is to be provided in the horizontal reinforcement of the foundation with FeZn strips of size 40x4mm throughout the perimeter, with 1 meter strip extensions in all four corners, price to include crosswise elements, related fittings and connections, and earth rods 1.5m in all 4 angles the two Harwall Units. (as per designs provided dwg A-21). | LS | 1 |  | 0
4 | Harwalls Erection Works
4.1 | Assemble Hardwall Units, complete, over the strip foundation, as per the designs provided. Hardwall Units will be provided by EULEX. The steel profiles have to be treated with anti rust paint and final paint coat 2x. | EA | 2 |  | 0
4.2 | Provide material, manufacture and install connection corridor between the two HardWall Units as per designs/details provided with the structure consisting of U and I profiles, covered with prepainted corrugated metal sheet th=0.55mm . Two openings to be created for the doors to be installed as per point 4.3 below. The metal profiles have to be treated with anti rust paint 2x and the final paint coat 2x. Prior to manufacturing all measurements must be taken on spot. Price is to include also flushings required where the corridor connects with Harwall Units at both ends and also gutters. (dwg A-21). | LS | 1 |  | 0
4.3 | Provide and install metal solid door as emergency exit door, equipped with anti panic push bar, with handle and possibility to close with a key from outside, dim 90x205cm. | EA | 2 |  | 0
4.4 | Provision and laying of plastic foil 0.2mm all over the floor surface. | m2 | 438.9 |  | 0
4.5 | Provide material and construct reinforced concrete slab for all three Rubb Halls th=15cm with C-30, net Q335 Ø8mm 15x15, over the compacted graveled surface ( Note: gravel layers 0-60, 0-30 are included within the infrastructure works). | m3 | 65.84 |  | 0
4.6 | Provide materials and lay epoxy two component flooring over the concrete slab, including skirting 12 cm high to the wall (price to include all the coating/layers materials and works). | m2 | 438.9 |  | 0
5 | Electrical Works
5.1 | Install main electrical panel for Hardwall Units (1 panel for both Units), complete, including grounding of the panel. Electrical panel will be provided by EULEX. | LS | 1 |  | 0
5.2 | Provide and install double tube florescent light with cover (bracket) 2x36W. Price shall include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking/ ducting pipes. Product suitable for use in warehouses. Lines to be organised in 4 separate lines per building | EA | 36 |  | 0
5.3 | Provide and install cabling for the Emergency EXIT lights as per dwg provided, 8W. Price shall include all the required trunking/ducting pipe, and any other required fittings for the installation. Emergency Exit lights will be provided by EULEX. | EA | 4 |  | 0
5.4 | Provide and install cabling for the emergency lights 2 x8W as per dwg provided, including all the trunking required and protection. Emergency lights will be provided by EULEX. | EA | 12 |  | 0
5.5 | Provide material and install external street lights 125W in corners of the building, as indicated in the provided layouts. Lights are to be installed in galvanised metal poles fixed on the structure/or with galvanised metal poles fixed to the ground. | EA | 2 |  | 0
5.6 | Provide and install rotating light switches | EA | 4 |  | 0
5.7 | Provide and install three phase sockets, complete with all the required fittings and cabling. All the cabling is to be covered with proper PVC trunking/ducting. | EA | 2 |  | 0
5.8 | Provide and install single phase double socket outlets, wall/panel mounted, 16A, 220V. Price shall include the cable type PPY 3x2.5mm2 and all the required fittings for functional sockets. Cable are to be covered with proper PVC trunkings | EA | 2 |  | 0
|  | Total all |  |  | 0
Note: | Prior to commencing the foundation works, the contractor is to check the issued Hardwall Units and verify the dimensions of the structure.

## Storage bld(ex carwash)
Storage Building (ex Car Wash) Reconstruction
Works Description
1 | Demolition/Dismantling works | Unit | Quantity | Unit price | Total price
1.1 | Dismantling of the metal door( in middle wall) Dismantled material to be transported to the town dump side. Dim. 110x210cm | EA | 1 |  | 0
1.2 | Dismantling of the big metal rolling doors complete with mechanism and control boxes . Dismantled material to be stored at Eulex store. Dim. ~ 400x400cm | EA | 8 |  | 0
1.3 | Demolition of the metal grill width 33cm from existing floor drain inside the bld. Debris to be transported to the town dump side. | m' | 40 |  | 0
|  |  |  | Total 1 | 0
2 | Construction works | Unit | Quantity | Unit price | Total price
2.1 | Supply with material, fulfilling and compaction of the existing inside drain channel 33x27cm with gravel 0-30mm up to level of existing concrete flooring in both rooms, length of the channel 40m'. | m3 | 3.5 |  | 0
2.2 | Provide with material and construct the concrete slab d=8cm with reinforcement steel ribbed mesh Q335 - Ø 8mm (sq.15x15cm). Slab to be smooth leveled | m3 | 28.8 |  | 0
2.3 | Supply with material and floor coating with primers, epoxy resin floor coatings, epoxy resin floor screeds & self-smoothing finishes, polyurethane floor coatings in the concrete floor from pos 2.2. Floor coating to be increase in the walls in whole perimeter in height 12 cm. Colour will be assigned by the Project Manager. | m2 | 360 |  | 0
2.4 | Provide with material and painting of the new siporex walls with primer and final in 2 layers of white dispersive high quality paint. | m2 | 131.56 |  | 0
2.5 | Supply with material and change broken glass termopan 4+12+4mm from existing metal windows. Dim. 131x 85cm | EA | 4 |  | 0
2.6 | Cutting of the existing support metal profiles in both fields where new rolling doors will be installed. Metal supports to be stored to the Eulex storage. | Ea | 2 |  | 0
2.7 | Supply with material and install new metal support columns ( I steel profile 160/80mm + □profile 100x100 mm - d=4mm) H= 4.60m in both sides of the new rolling doors. In the price to be calculated welding in upper existing construction and embed in the concrete base. Elements to be painted with anticorrosive paint 2x and final paint 2x. Measurements to be taken on the spot. | EA | 4 |  | 0
2.8 | Supply with material and construction of the wall d=20cm by siporex blocks. The price also includes lintels, concrete ring beams, reinforcement, formwork and shoring. | m2 | 133 |  | 0
2.9 | Plastering of the siporex new wall from both sides with plaster1:3:6 in two layers previously spreading manually the plaster concrete base in working surfaces. Final plaster surface to be smooth and uniformly. | m2 | 265 |  | 0
2.1 | Supply with material and install high quality metal rolling doors complete with mechanism and control boxes , with alternative operation possibility: electronically and mechanically. In this door to be incorporated small normal entry door dim. 90/210cm with lock. Measurements to be taken on the spot. Dim. 370x400+60cm | EA | 2 |  | 0
2.11 | Supply with material and install high quality solid metal emergency exit doors, equipped with push bar and self closer | Ea | 2 |  | 0
2.12 | Supply with material and install down part of the existing gutters to water away from the building foundation, gutter curved Ø100mm, length ~25cm. | Ea | 6 |  | 0
2.13 | Painting of the outside walls (new and existing)with facade washing dispersive paint, high quality. Colour will be assigned by the investor | m2 | 112.74 |  | 0
2.14 | Painting of the outside down part of the wall(cokla) in h=60cm with quality teraplast (kulir) plaster. Plaster to be waterproof, constant and resistant in all climate and atmospheric conditions. Colour will be assigned by the investor. In the price to be included repair of partially damaged existing plaster and primer base glued fibre glass reinforcement mesh. | M' | 26.6 |  | 0
|  |  |  | Total 2 | 0
TOTAL Storage Bld
1 | Demolition/Dismantling works | 0
2 | Construction works | 0
| Total all | 0
Note: | Clearance for any removal of debris from the site is to be taken from the Project Manager of EULEX.

## Plumbing
BoQ_ EEPC&EMC Plumbing Installations
| Work Description | Unit | Quantity | Cost Euro | Total Euro
1 | PLUMBING AND SEWAGE WORKS
1.1 | Site, route survey and staking the layout, pipe route with pickets. | M1 | 176
1.2 | Excavation in trenches to depth up to 1.20m, including shoring where necessary, storing on site of excavated material and removal of surplus material on completion. (Sewer pipes). | M3 | 120
1.3 | Leveling bottom of trenches to longitudinal profile, including removal of surplus material on completion. (Sewer pipes). | M2 | 75
1.4 | Excavation in trenches to depth up to 1.10m, including shoring where necessary, storing on site of excavated material and removal of surplus material on completion. (Water pipes). | M3 | 40
1.5 | 10cm thick sand setting bed to bottom of trenches, including leveling of upper surface and filling over pipes to a total of 40cm. | M3 | 35
1.6 | Backfill of the trenches with excavated material in 30 cm thk. compacted layers. Transportaion of surplus material to city landfill. | M3 | 113
1.7 | Cut asphalt and repair. | M2 | 12
1.8 | Connect AB units to water and sewer pipes. | EA | 2
1.9 | Provide and install PE OD20 cold water pipe including all necessary fittings. | M1 | 121
1.1 | Provide and install PE OD40 cold water pipe including all necessary fittings. | M1 | 29
1.11 | Provide and install 200mm PVC sewerage pipes. | M1 | 126
1.12 | Provide material and install pre-fabricate concrete elements for manhole with diameter ND1000/1000 and cones 600/1000 fixed on concrete base slab, including fulfilling of joints, complete waterproof. Heavy duty manhole metal cover included (standard heavy transport 25t). Iron steps included. | EA | 4
1.13 | Provide and install above ground cleanout for sewer pipes (DN110 PVC 4EA). | EA | 2
1.14 | Pressure test of new sewerage pipes (including internal pipes). | M1 | 126
1.15 | Pressure test of new water supply pipes. | M1 | 50
1.16 | Other unforeseen works (2% of above costs). | LS | 1
| 1. TOTAL PLUMBING WORKS |  |  |  | 0
2 | Ablution unit renovation type 1
2.1 | Provide and install new toilets complet with flushing tank and anal wash. (1EA AB unit). | EA | 4
2.2 | Provide and install new sinks with faucet, cabinet and mirror. (1EA AB unit). | EA | 2
2.3 | Provide and install new urinals complete with faucets. (1EA AB unit). | EA | 2
2.4 | Provide and install new floor drain. (1EA AB unit). | EA | 2
2.5 | Provide and install new 10L water heater including all necessary materials. (1EA AB unit). | EA | 1
2.6 | Provide and install OD PE16 cold water pipe including all necessary fittings. (1EA AB unit). | M1 | 8
2.7 | Provide and install PE OD20 cold water pipe including all necessary fittings. | M1 | 3.5
2.8 | Provide and install PVC DN50 pipe including all necessary fittings. | M1 | 3
2.9 | Provide and install PVC DN70 pipe all including all necessary fittings. | M1 | 6
2.1 | Provide and install PVC DN110 pipe all including all necessary fittings (including above ground cleanout). | M1 | 9
2.11 | Provide and install heat trace and insulation for 110 PVC sewerage pipe above the ground to entering point. (25 mm insulation and wrap with selfcontracting plastic foil). | M1 | 3
2.12 | Provide and install heat trace and insulation for OD 20 PE pipe above the ground to entering point. (25 mm insulation and wrap with selfcontracting plastic foil). | M1 | 3
2.13 | Pressure test of new plumbing installations. | LS | 1
2.14 | Plumbing complete as per items above 1EA AB Unit Type 1. | EA | 2
| 2. TOTAL AB Units type 1 |  |  |  | 0
3 | STORM DRAINAGE WORKS
3.1 | Site, route survey and staking the layout, pipe route with pickets. | M1 | 504
3.2 | Excavation in trenches to depth up to 1.20m, including shoring where necessary, storing on site of excavated material and removal of surplus material on completion. | M3 | 363
3.3 | Leveling bottom of trenches to longitudinal profile, including removal of surplus material on completion. | M2 | 302
3.4 | 10cm thick sand setting bed to bottom of trenches, including leveling of upper surface and filling over pipes to a total of 40cm. | M3 | 120
3.5 | Backfill of the trenches with excavated material in 30 cm thk. compacted layers. Transportaion of surplus material to city landfill. | M3 | 242
3.6 | Provide and install 200mm PVC sewerage pipes. | M1 | 275
3.7 | Provide and install 110mm PEHD drainage perforated pipe. | M1 | 230
3.8 | Provide material and fixing pre-fabricate concrete elements-gully's (open storm water outlets) with diameter ND400mm, fixed on concrete base slab, including fulfilling of joints, complete waterproof. Metal grid cover 400X400mm included. | EA | 12
3.9 | Provide material and install pre-fabricate concrete elements for manhole with diameter ND1000/1000 and cones 600/1000 fixed on concrete base slab, including fulfilling of joints, complete waterproof. Heavy duty manhole metal cover included (standard heavy transport 40t). Iron steps included. | EA | 5
3.1 | Cut asphalt and repair. | M2 | 6
3.11 | Pressure test of new sewerage pipes (of drainage network only). | M1 | 275
| 3. TOTAL DRAINAGE WORKS |  |  |  | 0
4 | Sprinkler Station and water main pipes
4.1 | Excavation in trenches to depth up to 1.20m, including shoring where necessary, storing on site of excavated material and removal of surplus material on completion. (Sewer pipes). | M3 | 56
4.2 | 10cm thick sand setting bed to bottom of trenches, including leveling of upper surface and filling over pipes to a total of 40cm. | M3 | 62
4.3 | Backfill of the trenches with excavated material in 30 cm thk. compacted layers. Transportaion of surplus material to city landfill. | M3 | 182
4.4 | Provide and install PE OD90 PN10 water pipe including all necessary fittings from sprinkler station to hardwalls and rubhalls. | M1 | 274
4.5 | Pressure test of new water main sprinkler pipes (PE OD90). | M1 | 274
| 4. TOTAL SPRINKLER STATION |  |  |  | 0
GRAND TOTAL plumbing and sprinklers statione
1 | Plumbing and sewage works |  |  |  | 0
2 | Ablution unit renovation type 1 |  |  |  | 0
3 | Storm drainage works |  |  |  | 0
4 | Sprinkler Station and water main pipes |  |  |  | 0
|  |  | GRAND TOTAL |  | 0

## Summary all
Summary
No | SUMMARY TABLE
1 | Office Block 1 | 0
2 | Office Block 2 | 0
3 | Infrastructure (roads, parking,electrical,heating plant/system) | 0
4 | Erection of Rubb Halls 1,2&3 | 0
5 | Erection of Hard Walls 1&2 | 0
6 | Storage building ( ex Carwash ) refurbishment | 0
7 | Plumbing Installations | 0
TOTAL |  | 0