[image: image1.jpg]—ULEX

European Union Rule of Law Mission

Kosovo





European Union Rule of Law Mission in Kosovo 
EULEX Kosovo

Ndertesa Farmed 

“Muharrem Fejza” p.n.

Lagja e Spitalit 

10 000 Pristina, Kosovo
Tel: + (386) 43 78 2000
http://www.eulex-kosovo.eu
CLARIFICATIONS (2)
PUBLICATION REFERENCE : EuropeAid/131122/M/WKS/XK
PROC/245/10/New Heating System  

1. Question regarding Administrative Issues 

	No
	Question
	Answer

	1


	Will a copy the Business Registration and the Tax Registration from Kosovo satisfy this requirement for evidence of status?  
	The Contracting Authority shall accept documents issued by a judicial or administrative authority in the country of origin or provenance showing that the requirements have been met.


	2
	Can a Tenderer “Self Declare” meaning write a declaration stating that they do not fall into any of the listed condition in the Practical Guide 2.3.3 Grounds for Exclusion, or will a declaration from the Municipal or District Court be required.


	Tenderers must duly complete the Tenderer’s Declaration (s), which is part of the Tender Form for Works Contracts (see Volume 1, Section 2 of the Tender Dossier).
Tenderers must provide declarations to the effect that they are not in any of the exclusion situations listed in section 2.3.3 of the Practical Guide to contract procedures for EC external actions. The declarations must cover all the members of a joint venture/consortium. Tenderers who have been guilty of making false declarations may also incur financial penalties and exclusion in accordance with section 2.3.4 of the Practical Guide. If the tenderer submits a self-declaration/statement as documentary proof, the Contracting Authority reserves the right to ask for further documentary evidence.

	3
	Will translation of supporting documents not in a one of the official EU languages need to be translated by an “official/certified translator
	If the supporting documents are not written in one of the official languages of the European Union, a translation into the language of the call for tender must be attached. Where the documents are in an official language of the European Union other than the one of the procedure, it is however strongly recommended to provide a translation into the language of the call for tenders, in order to facilitate the evaluation of the documents.

	4
	A Power of Attorney is typically signed by a Notary. There are no provisions in the current Kosovo Laws that provide for a Notary Service. Will a power of Attorney be countersigned by both parties involved in the joint venture be sufficient or will a signature and Stamp be required for the local Municipal or District Court?
	Tenderers must duly complete Form 4.3 of the Tender Dossier (Section 4: form 4.3, Power of Attorney). The aforesaid document must be must be signed, stamped and dated by all members of the joint venture/consortium. 


	5
	Will Audited Financial Statements for 2008. 2009 and 2010 satisfy the requirements? 


	Please attach copies of the company's previous 3 years certified statements of account (2010, 2009 and 2008).



	6
	Define “Legally Empowered Signatories”. Reference Question 4, the current Kosovo Statues does not provide for Notary Service.


	The tender must be signed in a way that legally binds all members. One member must be appointed lead member and that appointment confirmed by submission of powers of attorney signed by legally empowered signatories representing all the individual members. See Form 4.6.5 in Volume 1 and the tender form.



	7
	Separately, tenderers must quote, in Euro, the taxes, customs and import duties applicable at the time of submission. Were in the quote will this information be placed?
	Please disregard point 13.4 of the Instructions to Tenderers. 



	8
	Please clarify the original and each subsequent copy of the offer will be place into individual envelopes. Those envelopes will in turned be placed into one envelope.  A total of 5 envelopes for the offer and all copies are required
	The complete tender must be submitted in 1 (one) original, clearly marked "original" and 3 (three) copies, also clearly marked "copy". In the event of any discrepancy between them the original will prevail.

The envelopes should then be placed together in another sealed envelope/package.

	9
	Do we need to provide a Tender Guarantee of Euro 3,000.00 for 90 days?
	The tender guarantee must remain valid for 45 days beyond the period of validity of the tender, including any extensions, and be issued to the Contracting Authority for the requisite amount.

The tender guarantees of unsuccessful tenderers will be returned together with the information letter that the tenderer has been unsuccessful.

The tender guarantee of the successful tenderer shall be released when the tenderer has signed the contract and provided the requisite performance guarantee.


2. Question regarding Technical Specifications 
	No
	Question
	Answer

	1
	A container will be placed referred by your side during the period of site visit?
	The furnace should be containerized. The Container should as well be provided by the selected Contractor.  

	2
	Who will provide the 20' container for heating room and should this be insulated.
	The container has to be provided by the selected contractor. 

Yes, the container has to be insulated.  

	3
	No housing is foreseen at the boilers and sub-station position. If any housing is to be constructed, please inform us about its material, dimensions and which BoQ item should include its price?
	20 feet Insulated Container (605x244cm) is to be provided as housing. 
The price should be included under point I1 and I2 of the BOQ. 

	4
	Which BoQ item should include the protecting wall around the oil tanks?


	Protecting wall (containment tank) should be included under point I22 of the BOQ (consolidated BOQ).

	5
	No manholes are foreseen at the connection places of the blocks to the main network. If these are to be constructed, please inform us about "the detail" and which BoQ item should include its price?
	No manholes are foreseen.

Spherical valves for shutting down the system are foreseen at the entry of each Block
 (Building)  

	6
	In tender specification it has not been foreseen place for boiler room, has this position been forgotten, and who has obligation to perform this work ?
	As specified under point 5.1.3 of Technical Specifications both furnaces should be containerized units.  The selected contractor is obliged to provide the containers and perform the works ( see above point 3)

	7
	In specification there have been planned pre-isolation pipes, but there haven’t been planned any pre-isolated bends and the following fitting?
	Included under point I 20 of the BOQ ( 30% from position I17 and I19) 

	8
	Can you please provide us existing plan of canalization distribution pipes of object and distribution of electrical network in the object, due to pacification of future works foreseen in tender.
	The plans that we posses for the underground water, sewerage, electricity network are not up to date.   

Therefore we cannot rely on their accuracy. 

	9
	We would like to please you if you can send us the other answers on questions that have been made by other companies because this would help us in completing of our offer.
	Please refer to Clarifications and Corrigendum No.2  

	10
	The estimated thickness of the APSHALT that will need to be replaced. This information is needed to price the total amount of Asphalt
	Estimated thickness of asphalt within the Camp is 8cm. 

	11
	The Scope of Work states that the copper pipe needs to be painted WHITE. Can you verify this? Normally copper piping is not painted.
	It remains as stated with Scope of Works. 

	12
	Can a alternate to pipe routing be proposed if it would mean a cost savings to EULEX. The same material and quality meeting the stated outcomes/Standards will be achieved.
	Please stick to the provided design for the pipe routing. 

	13
	In “Bill of Quantities” we have ( pos. nr.I.6 )17 pumps, but in drawings we can see just 8 of them.
	The number in BOQ is correct (17 pumps).  Each building is planned to have its own secondary pump. 

	14
	In “Bill of Quantities” ( pos. nr.I.27 ) we have Chimney 6 pieces, but in the other side we have two boilers for central heating (hot water production) with fuel.
	Correct, there should be two chimneys, one for each block. 
Please refer to the Corrigendum No.2

	15
	In “Bill of Quantities” we have (pos. nr.II.1 ) in total 327 radiators, in Annex_6b we have total 328 radiators, but in drawings I can see 330 radiators.
	Please refer to Corrigendum No.2.

	16
	Does the front of each building should have hole with cover with valves? So they can exclude any of the objects individually in the case of intervention
	No manholes are foreseen. Valves for shutting down the system for each building are foreseen close to the secondary pumps, in the corridor.  

	17
	In this point 4.4.7 we need to have more clarification (Protection of Existing Works and Services)

Will we have a clear layout map with the position of existing services such as sewers, water pipe, cables for electricity and telephone, telephone and lighting, poles etc. 

If not, who will take responsibility of damages?
	The plans that we possess for the underground water, sewerage, electricity network are not up to date.  Therefore we cannot rely fully on their accuracy. 

Those plans will be provided to the contractor. 

The responsibility of damages is clearly explained on the afore mentioned point 4.4.7 




Eot.
PAGE  

