European Union Rule of Law Mission in Kosovo

EULEX Kosovo

Ndertesa Farmed

“Muharrem Fejza” p.n.

Lagja e Spitalit

10000 Pristina, Kosovo

www.eulex-kosovo.eu

- CORRIGENDUM NUMBER 1

- TO THE TENDER DOSSIER

- PUBLICATION REFERENCE: PROC/1056/21/Reorganisation of ECM Mitrovica

The following corrections are made to the Tender Dossier

- The following corrections are made to the Technical Specifications:

- The former text:

- Part of parking cover attached to the Helipad T Walls is to be cut, see dwg #02, cut is to be done in length of app. 1m (roof cover, truss and columns). Cut columns are to be relocated for 1m’ and welded in cube foundation which will also be built as described in BoQ.

- There is the underground PE septic tank capacity 3000 l, located nearby cafeteria, which is to be dismantled, area to be cleaned and debris to be sent out of the compound. In the same place, bigger septic with capacity of 1000 l is to be provided and installed. This means that more excavation is needed for the placement of the new tank where the new sewerage network will be connected (see technical description under infrastructure works)

- NOTE: Prior removal of the debris from the site, approval must be obtained from the Project Manager.

- Shall read now:

- Part of parking cover attached to the Helipad T Walls is to be cut, see dwg #02, cut is to be done in length of app. 1m (roof cover, truss and columns). Cut columns are to be relocated for 1m’ and welded in cube foundation which will also be built as described in BoQ.

- There is the underground PE septic tank capacity 3000 l, located nearby cafeteria, which is to be dismantled, area to be cleaned and debris to be sent out of the compound. In the same place, bigger septic with capacity of 10000 l  is to be provided and installed. This means that more excavation is needed for the placement of the new tank where the new sewerage network will be connected (see technical description under infrastructure works)

- NOTE: Prior removal of the debris from the site, approval must be obtained from the Project Manager.

- The former text:

…..PE Septic Tank with capacity of 1000L for SSD block & for BI guards Ablution is to be provided and installed underground in the place where the old one is taken out, including excavation works (~ 6m3 of earth), backfilling works after tank installation and top protection of the tank with reinforcement concrete slab with Q 226 mesh (slab dim ~250x250x10cm), with movable steel cover for the shaft opening. See photos below as example:…….

- Shall read now:

- ……PE Septic Tank with capacity of 10000L for SSD block & for BI guards Ablution is to be provided and installed underground in the place where the old one is taken out, including excavation works (~ 6m3 of earth), backfilling works after tank installation and top protection of the tank with reinforcement concrete slab with Q 226 mesh (slab dim ~250x250x10cm), with movable steel cover for the shaft opening. See photos below as example:……..

- The following corrections are made to the Bill of Quantities 5. Fence and Infrastructure (5.7):

- The former text:

| Reorganization of Mitrovica ECM |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 5 | T walls - fence and infrastructure works |  |  |  |  |
|  | Works Description | Unit | Quantity | Unit price | Total price |
| 5.1 | Relocation of T walls within the same Compound- from their current position to the new identified position as per existing and new designs provided creating the new division for the partial handover of the Camp. T wall footing 1.6m wide, T wall high 3.00m, length 1.5m'. Gravel bases needed to be provided and placed by contractor and is to be included in the price. | EA | 69.00 |  | 0.00€ |
| 5.2 | Transportation of T walls from ECM to Prishtina EPC/ Dumosh TEC. T wall footing 1.6m wide, T wall high 3.00m, length 1.5m'. T walls are to be unloaded in the site designated by the project engineer. | EA | 73.00 |  | 0.00€ |
| 5.3 | Provide with material and construction of new wall h 250 + V steel profiles and concertina wire ofᴓ 60cm( same as existing perimeter wall of entire camp), see dwg # 27, price to include excavation works in asphalted/concreted area and backfilling works around foundations. | m' | 118.00 |  | 0.00€ |
| 5.4 | Provide with material and construction of new fence icluding V steel profiles and concertina wire ᴓ 60cm, all according to dwg # 27, Fence is to be installed on top of the remain wall in right side of vehicle entry( see item 2.3). | M' | 25.50 |  | 0.00€ |
| 5.5 | Dismantle the 2.2m high fence around the heating plant near by block 7 and save on site for further use (10m' are to be reused-see pos. below, other 10m' are to be taken off from the compound.) | m' | 20.00 |  | 0.00€ |
| 5.6 | Installation of dismantled fence from the previous pos, in new location, around the waste containers, adjusting the fence as needed with welding, paintig,and construction od new cube concrete foundations 40x40x30 +10cm compacted gravel, every ~3m' with anchored steel plate 200x200x5mm on top of cube foundation.. | m' | 10.00 |  | 0.00€ |
| 5.7 | Provide with material and install the underground PE Septic tank for SSD block & for BI guards Ablution with capacity of 1000L. Septic Tank to be installed in the same place where the old one with smaller capacity is dismantled. In the price to be calculated excavation works( ~ 6m3 of earth), backfilling works after tank installation and top protection of the tank with reinforcement concrete slab with Q 226 mesh ( slab dim 250x250x10cm), with steel cover for the shaft . See tech. specs for more details. | EA | 1.00 |  | 0.00€ |
|  | Plumbing (Water &Sewerage) - exterior |  |  |  |  |
| 5.8 | Conduct site survey and marking of the trench line on terrain as per the drawing provided for water and sewerage lines. | LS | 1.00 |  | 0.00 € |
| 5.9 | Cutting of asphalt for the trench with adequate asphalt cutting machine, and removal of the cut asphalt from the site (asphalted trench length 92m) | m' | 106.00 |  | 0.00 € |
| 5.10 | Removing the concrete pavement block , storing on site and reinstall again after finishing with canal works with installations. | M2 | 5.00 |  | 0.00 € |
| 5.11 | Excavation of trenches to depth up to average 80 cm, over the entire route length with adequate excavator machine. Note and include in the price that under 20cm of land level exist underground reforcement concrete slab 20-30cm thickness that is to be broken, to create required depth of the tranch. Tranch as per marked line in dwg.#2. Excavated material is to be temporary storingon site, to be reused for backfilling. (total trench length 60m') Leftover material should be disposed of by the contractor from the site | m3 | 40.00 |  | 0.00 € |
| 5.12 | Provide materials and lay 10cm thick sand bed (0.5-2mm grain size) to bottom of trenches, including leveling of upper surface and filling over pipes to a total of 30cm. | m3 | 15.00 |  | 0.00 € |
| 5.13 | Provide and install PVC sewerage pipe 120mm for SSD and Toilet for BI guards- from objects to the septic tank and for FPU Commander Block- from object to the existing sewerage system. Calculation to be done for all exterior works including entry to the premises. | m' | 60.00 |  | 0.00 € |
| 5.14 | Cut the concrete slab, open the hole ~100x100cm in depth of ~120cm, to reach the existing water supply pipe of 2". In same place is to be build the manhole (foreseen in Item 5.15) | LS | 1.00 |  | 0.00 € |
| 5.15 | Provide and connect new PE 1" water pipe into the existing main pipe of 2", including all the accessories/fittings for conection. Calculation to be done for all exterior works including entry to the premises. | m' | 60.00 |  | 0.00 € |
| 5.16 | Provide and install pre-fabricate concrete elements for manhole with diameter 1000/1000 & 600/1000 fixed on concrete base, including filling of joints, complete waterproof. Heavy duty manhole metal cover included (standard heavy transport 25t). Price to include excavation and refilling works | EA | 7.00 |  | 0.00 € |
| 5.17 | Backfill the trenches with excavated material in 20 cm thick compacted layers. Surplus material is to be disposed outside EULEX compound. | m3 | 25.00 |  | 0.00 € |
| 5.18 | Provision and installation of the sewerage underground warning tape throughout the trench, 30 cm below the finished surface. | m' | 60.00 |  | 0.00 € |
| 5.19 | Provision and installation of the water underground warning tape, 30 cm below the finished surface. | m' | 60.00 |  | 0.00 € |
| 5.20 | Providing and spreading gravel, particle size 0-30 mm on previously compacted sub-base and compacting to form a final base course of 250mm thickness. Compacting to be done with power roller note: total amount of the gravel is to be calculated in final compacted state | m3 | 25.00 |  | 0.00 € |
| 5.21 | Placing back the peevishly removed concrete pavement blocks ( point 1.3) | m2 | 20.00 |  | 0.00 € |
| 5.22 | Provide and spread layer of bitumen emulsion (hot coat) above base course of compacted gravel, average 0,8kg/m2 for better connection between road base course and layer of asphalt. | m2 | 48.00 |  | 0.00 € |
| 5.23 | Provide material and laying of asphalt layer 80mm finished thickness after consolidation by power roller , mixture 0-16mm including compaction. | m2 | 48.00 |  | 0.00 € |
| 5.24 | Provision and installation of heat trace for all over ground pipes/ entry points to the premises. | m' | 12.00 |  | 0.00 € |
| 5.25 | Insulation of all over ground pipes/entry points to the buildings | LS | 1.00 |  | 0.00 € |
|  | Electrical |  |  |  |  |
| 5.26 | Cutting of asphalt for the trench with adequate asphalt cutting machine, and removal of the cut asphalt from the site. | m' | 90.00 |  | 0.00 € |
| 5.27 | Removing the concrete pavement block , storing on site and reinstall again after finishing with canal works with installations. | M2 | 9.50 |  | 0.00 € |
| 5.28 | Excavation of trenches 60 cm wide and 60 cm deep for the underground cabling. Note and include in the price that under 20cm of land level exist underground reforcement concrete slab 20-30cm thickness that is to be broken, to create required depth of the trench. Trench as per marked line in dwg.#2 , total 73m' (due to the many underground cables, hand excavation nearby the server room is to be foreseen) | m3 | 26.30 |  | 0.00 € |
| 5.29 | Provide material and laying of sand base (under, around and over the ducting pipes, 20cm ) throughout the all trenches. | m3 | 8.80 |  | 0.00 € |
| 5.30 | Provide and install ducting corrugated pipe Ø75mm equipped with rope/wire, throughout the trenches, from main electrical panel installed in Reception(see pos. 5.30) to the electrical panels of : Reception block, SSD block, Server room#8, containers for reserve food and water and up to the second entry gate (see dwg.#2) In every trench are to be installed 3 ducting pipes, one of them will be used for IT and Comms cabling. | m' | 330.00 |  | 0.00 € |
| 5.31 | Provide material and construct concrete manhole complete 1000 depth dim1000x1000m , including heavy duty metal covers 600x600mm (25T) and other required works to make the manholes functional - for purpose of laying down all the installations to the buildings. | EA | 2.00 |  | 0.00 € |
| 5.32 | Provide with material and install Electrical Panel #1withIP65, equipped with cartridge 250A and knife fuses 3pcs. Grounding of the panel, to be done with copper rod | EA | 1.00 |  |  |
| 5.33 | Disconnect the existing electrical cable NYY-J (PP00) 4x120mm2 Copper from block#7, pull the cabling from the shaft nearby reception block and redirect the cable to word the Reception block as shown in dwg#2. Cable is to be connected to the electrical panel #1 from pos.5.31. Price to include all necessary fittings for connection. | LS | 1.00 |  | 0.00 € |
| 5.34 | Provide material and install underground cable 4x16mm2 (Cu) from electrical panel #1 up to el.panels of SSDblock, Reception block, Server Room#8, two security containers and up to the second entry gate. Price to include connection of the cables in both ends with all necessary fittings. | m' | 80.00 |  | 0.00 € |
| 5.35 | Backfill the trenches with excavated material in 20 cm thick compacted layers. Surplus material is to be disposed outside EULEX compound. | m3 | 8.80 |  | 0.00 € |
| 5.36 | Supply and laying of the underground warning tape throughout the all trenches. | m' | 80.00 |  | 0.00 € |
| 5.37 | Providing and spreading gravel, particle size 0-30 mm on previously compacted sub-base and compacting to form a final base course of 20cm thickness. Compacting to be done with power roller note: total amount of the gravel is to be calculated in final compacted state | m3 | 8.80 |  | 0.00 € |
| 5.38 | Provide and spread layer of bitumen emulsion (hot coat) above base course of compacted gravel, average 0,8kg/m2 for better connection between road base course and layer of asphalt. | m2 | 44.00 |  | 0.00 € |
| 5.39 | Provide material and laying of asphalt layer 80mm finished thickness after consolidation by power roller , mixture 0-16mm including compaction. | m2 | 44.00 |  | 0.00 € |
| 5.42 | Dismantling of existing steel poles100x100mm, 6m high togethet with reflectors and censors, from Twalls and installation of the same to the new Twall/wall fence line together with lights/reflectors censor, as per instruction of site Engineer. Price to include painting of the poles with primary and final oil paint . | EA | 5.00 |  | 0.00€ |
| 5.43 | Provide and install new elect. Cable for the fence reflectors 5x2.5mm. Cabling is to be o be covered with proper PVC trunking. | m' | 200.00 |  | 0.00€ |
| 5.44 | Provide and install new elect. Cable for the fence reflectors 3x1.5mm. Cabling is to be covered with proper PVC trunking. | m' | 100.00 |  | 0.00€ |
| 5.45 | Dismantling of existing steel poles 100x100mm, 6m high together with cameras from Twalls and reinstallation of the same to the new Twall/wall /fence line together with cameras, as per instruction of site Engineer. Price to include painting of the poles with primary and final oil paint . | EA | 4.00 |  | 0.00€ |
|  |  |  |  | Total | 0.00€ |

- Shall read now:

Reorganization of Mitrovica ECM – 5.7. 5; T walls - fence and infrastructure works. Works Description; Unit; Quantity; Unit price; Total price. 5.1; Relocation of T walls within the same Compound- from their current position to the new identified position as per existing and new designs provided creating the new division for the partial handover of the Camp. T wall footing 1.6m wide, T wall high 3.00m, length 1.5m'. Gravel bases needed to be provided and placed by contractor and is to be included in the price.; EA; 69.00; 0.00€. 5.2; Transportation of T walls from ECM to Prishtina EPC/ Dumosh TEC. T wall footing 1.6m wide, T wall high 3.00m, length 1.5m'. T walls are to be unloaded in the site designated by the project engineer.; EA; 73.00; 0.00€. 5.3; Provide with material and construction of new wall h 250 + V steel profiles and concertina wire ofᴓ 60cm( same as existing perimeter wall of entire camp), see dwg # 27, price to include excavation works in asphalted/concreted area and backfilling works around foundations.; m'; 118.00; 0.00€. 5.4; Provide with material and construction of new fence icluding V steel profiles and concertina wire ᴓ 60cm, all according to dwg # 27, Fence is to be installed on top of the remain wall in right side of vehicle entry( see item 2.3).; M'; 25.50; 0.00€. 5.5; Dismantle the 2.2m high fence around the heating plant near by block 7 and save on site for further use (10m' are to be reused-see pos. below, other 10m' are to be taken off from the compound.); m'; 20.00; 0.00€. 5.6; Installation of dismantled fence from the previous pos, in new location, around the waste containers, adjusting the fence as needed with welding, paintig,and construction od new cube concrete foundations 40x40x30 +10cm compacted gravel, every ~3m' with anchored steel plate 200x200x5mm on top of cube foundation..; m'; 10.00; 0.00€. 5.7; Provide with material and install the underground PE Septic tank for SSD block & for BI guards Ablution with capacity of 10000L. Septic Tank to be installed in the same place where the old one with smaller capacity is dismantled. In the price to be calculated excavation works( ~ 6m3 of earth), backfilling works after tank installation and top protection of the tank with reinforcement concrete slab with Q 226 mesh ( slab dim 250x250x10cm), with steel cover for the shaft . See tech. specs for more details.; EA; 1.00; 0.00€. Plumbing (Water &Sewerage) - exterior. 5.8; Conduct site survey and marking of the trench line on terrain as per the drawing provided for water and sewerage lines.; LS; 1.00; 0.00 €. 5.9; Cutting of asphalt for the trench with adequate asphalt cutting machine, and removal of the cut asphalt from the site (asphalted trench length 92m); m'; 106.00; 0.00 €. 5.10; Removing the concrete pavement block , storing on site and reinstall again after finishing with canal works with installations.; M2; 5.00; 0.00 €. 5.11; Excavation of trenches to depth up to average 80 cm, over the entire route length with adequate excavator machine. Note and include in the price that under 20cm of land level exist underground reforcement concrete slab 20-30cm thickness that is to be broken, to create required depth of the tranch. Tranch as per marked line in dwg.#2. Excavated material is to be temporary storingon site, to be reused for backfilling. (total trench length 60m') Leftover material should be disposed of by the contractor from the site; m3; 40.00; 0.00 €. 5.12; Provide materials and lay 10cm thick sand bed (0.5-2mm grain size) to bottom of trenches, including leveling of upper surface and filling over pipes to a total of 30cm.; m3; 15.00; 0.00 €. 5.13; Provide and install PVC sewerage pipe 120mm for SSD and Toilet for BI guards- from objects to the septic tank and for FPU Commander Block- from object to the existing sewerage system. Calculation to be done for all exterior works including entry to the premises.; m'; 60.00; 0.00 €. 5.14; Cut the concrete slab, open the hole ~100x100cm in depth of ~120cm, to reach the existing water supply pipe of 2". In same place is to be build the manhole (foreseen in Item 5.15); LS; 1.00; 0.00 €. 5.15; Provide and connect new PE 1" water pipe into the existing main pipe of 2", including all the accessories/fittings for conection. Calculation to be done for all exterior works including entry to the premises.; m'; 60.00; 0.00 €. 5.16; Provide and install pre-fabricate concrete elements for manhole with diameter 1000/1000 & 600/1000 fixed on concrete base, including filling of joints, complete waterproof. Heavy duty manhole metal cover included (standard heavy transport 25t). Price to include excavation and refilling works; EA; 7.00; 0.00 €. 5.17; Backfill the trenches with excavated material in 20 cm thick compacted layers. Surplus material is to be disposed outside EULEX compound.; m3; 25.00; 0.00 €. 5.18; Provision and installation of the sewerage underground warning tape throughout the trench, 30 cm below the finished surface.; m'; 60.00; 0.00 €. 5.19; Provision and installation of the water underground warning tape, 30 cm below the finished surface.; m'; 60.00; 0.00 €. 5.20; Providing and spreading gravel, particle size 0-30 mm on previously compacted sub-base and compacting to form a final base course of 250mm thickness. Compacting to be done with power roller note: total amount of the gravel is to be calculated in final compacted state; m3; 25.00; 0.00 €. 5.21; Placing back the peevishly removed concrete pavement blocks ( point 1.3); m2; 20.00; 0.00 €. 5.22; Provide and spread layer of bitumen emulsion (hot coat) above base course of compacted gravel, average 0,8kg/m2 for better connection between road base course and layer of asphalt.; m2; 48.00; 0.00 €. 5.23; Provide material and laying of asphalt layer 80mm finished thickness after consolidation by power roller , mixture 0-16mm including compaction.; m2; 48.00; 0.00 €. 5.24; Provision and installation of heat trace for all over ground pipes/ entry points to the premises.; m'; 12.00; 0.00 €. 5.25; Insulation of all over ground pipes/entry points to the buildings; LS; 1.00; 0.00 €. Electrical. 5.26; Cutting of asphalt for the trench with adequate asphalt cutting machine, and removal of the cut asphalt from the site.; m'; 90.00; 0.00 €. 5.27; Removing the concrete pavement block , storing on site and reinstall again after finishing with canal works with installations.; M2; 9.50; 0.00 €. 5.28; Excavation of trenches 60 cm wide and 60 cm deep for the underground cabling. Note and include in the price that under 20cm of land level exist underground reforcement concrete slab 20-30cm thickness that is to be broken, to create required depth of the trench. Trench as per marked line in dwg.#2 , total 73m' (due to the many underground cables, hand excavation nearby the server room is to be foreseen); m3; 26.30; 0.00 €. 5.29; Provide material and laying of sand base (under, around and over the ducting pipes, 20cm ) throughout the all trenches.; m3; 8.80; 0.00 €. 5.30; Provide and install ducting corrugated pipe Ø75mm equipped with rope/wire, throughout the trenches, from main electrical panel installed in Reception(see pos. 5.30) to the electrical panels of : Reception block, SSD block, Server room#8, containers for reserve food and water and up to the second entry gate (see dwg.#2) In every trench are to be installed 3 ducting pipes, one of them will be used for IT and Comms cabling.; m'; 330.00; 0.00 €. 5.31; Provide material and construct concrete manhole complete 1000 depth dim1000x1000m , including heavy duty metal covers 600x600mm (25T) and other required works to make the manholes functional - for purpose of laying down all the installations to the buildings.; EA; 2.00; 0.00 €. 5.32; Provide with material and install Electrical Panel #1withIP65, equipped with cartridge 250A and knife fuses 3pcs. Grounding of the panel, to be done with copper rod; EA; 1.00. 5.33; Disconnect the existing electrical cable NYY-J (PP00) 4x120mm2 Copper from block#7, pull the cabling from the shaft nearby reception block and redirect the cable to word the Reception block as shown in dwg#2. Cable is to be connected to the electrical panel #1 from pos.5.31. Price to include all necessary fittings for connection.; LS; 1.00; 0.00 €. 5.34; Provide material and install underground cable 4x16mm2 (Cu) from electrical panel #1 up to el.panels of SSDblock, Reception block, Server Room#8, two security containers and up to the second entry gate. Price to include connection of the cables in both ends with all necessary fittings.; m'; 80.00; 0.00 €. 5.35; Backfill the trenches with excavated material in 20 cm thick compacted layers. Surplus material is to be disposed outside EULEX compound.; m3; 8.80; 0.00 €. 5.36; Supply and laying of the underground warning tape throughout the all trenches.; m'; 80.00; 0.00 €. 5.37; Providing and spreading gravel, particle size 0-30 mm on previously compacted sub-base and compacting to form a final base course of 20cm thickness. Compacting to be done with power roller note: total amount of the gravel is to be calculated in final compacted state; m3; 8.80; 0.00 €. 5.38; Provide and spread layer of bitumen emulsion (hot coat) above base course of compacted gravel, average 0,8kg/m2 for better connection between road base course and layer of asphalt.; m2; 44.00; 0.00 €. 5.39; Provide material and laying of asphalt layer 80mm finished thickness after consolidation by power roller , mixture 0-16mm including compaction.; m2; 44.00; 0.00 €. 5.42; Dismantling of existing steel poles100x100mm, 6m high togethet with reflectors and censors, from Twalls and installation of the same to the new Twall/wall fence line together with lights/reflectors censor, as per instruction of site Engineer. Price to include painting of the poles with primary and final oil paint .; EA; 5.00; 0.00€. 5.43; Provide and install new elect. Cable for the fence reflectors 5x2.5mm. Cabling is to be o be covered with proper PVC trunking.; m'; 200.00; 0.00€. 5.44; Provide and install new elect. Cable for the fence reflectors 3x1.5mm. Cabling is to be covered with proper PVC trunking.; m'; 100.00; 0.00€. 5.45; Dismantling of existing steel poles 100x100mm, 6m high together with cameras from Twalls and reinstallation of the same to the new Twall/wall /fence line together with cameras, as per instruction of site Engineer. Price to include painting of the poles with primary and final oil paint .; EA; 4.00; 0.00€. Total; 0.00€.

Please note that the consolidated version of the bill of quantities for is attached to the email.

- All other terms and conditions remain the same.

- EoT